## Slide 1
소듐냉각고속로(SFR)와 경수로의 NSSS 특성비교
- 소듐냉각고속로(SFR), 경수로와 무엇이 다른가? -
2015. 10. 28
이 태 호
Notes: <number>

## Slide 2
목 차
NSSS Characteristics
I
Safety-related Systems
II
Notes: <number>

## Slide 3
NSSS Characteristics
I

## Slide 4: Overall Configuration
PWR (Pressurized Water Reactor)
  Relatively low temperature configuration (compared with SFR) with high pressure design
  Water coolant
  One coolant loop
SFR (Sodium cooled Fast Reactor)
  High temperature configuration with ordinary pressure design
  Sodium coolant
  (high thermal efficiency)
  Two coolant loop (PHTS & IHTS)
  Employing IHTS to mitigate SWR consequences

## Slide 5: Coolant System of PWR
RCS configuration
  4-loop type (N-loop type): 4 HL, 4 CL, 4 SG, 4 RCP
  Framatome (P4, N4), AREVA (EPR), MHI (APWR)]
  2x4 loop type: 2 HL, 4 CL, 2 SG, 4 RCP
  OPR1000/APR14000; AP600/AP1000
Operating pressure & temperature
  Core outlet temperature: 320~330 oC
  Temp. increase through core: 30~40 oC
  Subcooling: ~20 oC at HL
  Pressure: 15~16 MPa (Controlled by PZR)
Basically saturated steam Rankine cycle as power conversion system
  Efficiency: ~32%

## Slide 6: Coolant System of SFR (1/2)
PHTS/IHTS configuration
  Pool type
  Prevent sodium leakage by locating primary pumps and IHXs inside RV
  Elimination of primary piping
  Mild transient response due to large thermal capacity of sodium
  Reduce reactor vessel (RV) penetrations
  Difficult in inspection/maintenance due to many components inside RV
  Phenix, BN-600, PFBR, BN-800, Super Phenix, PRISM
  Loop type
  Easy inspection/maintenance for primary pump, IHX, and primary piping
  Good natural circulation characteristics
  Penetrations on RV and longer piping
  Rapid tran. response compared to pool type
  BN-350, CRBR, MONJU

## Slide 7: Coolant System of SFR (2/2)
Operating pressure & temperature
  Core outlet temperature: 500~550 oC
  Temp. increase through core: 130~170 oC
  Pressure: ~0.1 Mpa
  Sodium boiling temp.: 883 oC
Superheated steam Rankine cycle as power conversion system
  Efficiency: ~40%

## Slide 8: Overall Arrangement
<SFR- Pool type PGSFR>
<PWR-2x4 loop type>

## Slide 9: Arrangement inside Reactor Vessel
IHX
<PWR>
<SFR- Pool type PGSFR>

## Slide 10: Main Components of PWR
<U-tube steam generator>
<RCP>
Shaft Seal Type
  Vertical, single-stage, centrifugal with controlled leakage shaft seals
  [Ex] APWR, APR1400
Canned-Motor Type
  Non-sealed: [Ex] AP600/AP1000
<Pressurizer>

## Slide 11: Main Components of SFR (1/2)
<IHX>
<Sodium pump>
Mechanical pump
EM pump

## Slide 12: Main Components of SFR (2/2)
<Steam generator>
<IVTM & Rotating plug
- Handling fuel assembly inside RV>
<Upper internal structure - Supporting
guide tubes of instrumentation and CRDM>

## Slide 13
Safety-related Systems
II

## Slide 14: PWR Systems (1/3)
Safety injection system
  Supply borated water during LOCA
  Remove decay heat and long term cooling after LOCA
  Supply borated water during RCS overcooling event such as MSLB accident
  Enable Feed-and-Bleed operation along with Safety Depressurization System
  Mainly consist of HPSI pump, SIT or Accumulator, LPSI pump
Shutdown cooling system
  Remove residual heat after RCS temperature & pressure are decreased
  Provide LTOP (Low Temperature Overpressure Protection) of RCS
  Enable Long Term Cooling (LTC) in conjunction with LOCA with IRWST
  Mainly consist of SC pump, SC heat exchanger
Auxiliary feedwater system
  Remove residual heat through steam generator until SCS can initiate the operation

## Slide 15: PWR Systems (2/3)

## Slide 16: PWR Systems (3/3)
Safety depressurization system
  Classical PWRs
  RDT: Rx Drain Tank
  PRV: Press. Relief Valve
  APR1400
  Safety Depressurization & Venting System
  Operated along with IRWST
    TLOFW: Feed-Bleed Operation
  AP600/AP1000
  ADS: Automatic Depressurization System
  ADS-1,2,3 & -4

## Slide 17: SFR Systems (1/5)
Decay Heat Removal System (DHRS)
  Remove decay heat after reactor shutdown
  Use of air cooling for ultimate heat sink
  Maximize natural circulation capability of sodium due to large temperature difference between heat source & sink
    Easy to implement passive & economic features
    Long grace without any active components

## Slide 18: SFR Systems (2/5)
  DHRS option
<RVACS>
<SGACS>

## Slide 19: SFR Systems (3/5)

## Slide 20: SFR Systems (4/5)
Sodium-Water Reaction Pressure Relief System (SWRPRS)
  Mitigate the consequence of large SWR in SG by relieving the pressure caused by produced hydrogen
    Can be design as non-safety system
    large leak in SG → pressure increase due to hydrogen → rupture disk bursts → discharge SWR product to sodium dump tank, SG isolation, drain steam/water inside SG into water dump tank → purge SG with N2 gas
  SG leak is detected by hydrogen meter (small leak), pressure gauge (medium leak) and rupture disk (large leak)

## Slide 21: SFR Systems (5/5)
  SG leak detection and action